## Tank Venting
Enviroment factor (F-Factor)
This document is confidential proprietary and/or legally privileged, intended to be used within PTTME Co.,Ltd. Unintended recipients are not allowed to distribute,copy, modify, retransmit, disseminate or use this document and/or information. | ATMOSPHERIC AND LOW PRESSURE STORAGE TANK VENTING CALCULATION | [42 empty] | Tank design : |  |  | #DIV/0!
[49 empty] | Insulation Conductance (W/m2K) | [5 empty] | Insulation thickness (mm) |  |  |  |  | table |  |  | F-factor
|  | TANK NO. | [9 empty] | DESCRIPTION. | [31 empty] | Bare metal tank/water application/Depressuring | [18 empty] | 1
[34 empty] | Bare Metal Tank (No Insulation) | [9 empty] | Insulated tank/Concrete |  |  |  |  | 1.9 | [5 empty] | 305 |  |  |  | 1 | 6.2295 |  |  | 0.025 |  | 1 |  |  | #DIV/0!
|  | I. INPUT | [24 empty] | Similar to Hexane | [6 empty] | Insulated tank - Fully Insulation | [14 empty] | 2.3 | [5 empty] | 254 |  |  |  | 2 | 9.0551 |  |  | 0.03 |  | 2
|  |  | TANK DETAIL | [11 empty] | FLUID PROPERTIES | [11 empty] | Similar to Hexane | [6 empty] | Insulated tank - Partial Insulation | [14 empty] | 2.8 | [5 empty] | 203 |  |  |  | 3 | 13.7931 |  |  | 0.0375 |  | 3 |  |  | #DIV/0!
|  |  | Tank Diameter | [6 empty] | mm |  | 24000 |  |  | Avg. Storage Temperature |  |  |  |  | °C |  | 35 |  |  |  |  | Higher than Hexane | [6 empty] | Concrete tank or Fire proofing | [14 empty] | 3.8 | [5 empty] | 152 |  |  |  | 4 | 25 |  |  | 0.05 |  | 4
|  |  | Tank Height (TL-TL) | [6 empty] | mm |  | 17500 |  |  | Vapour Pressure |  |  |  | 5.6 | kPa |  | Similar to Hexane |  |  |  |  | Unknown | [6 empty] | Water-application facilities | [14 empty] | 5.7 | [5 empty] | 102 |  |  |  | 5 | 55.8824 |  |  | 0.075 |  | 5
|  |  | Max. Tank Volume | [6 empty] | m3 |  | 7916.8135 |  |  | Flash Point or Boiling Point |  |  |  |  | °C |  |  | true |  | (F.P) | [8 empty] | Depressuring and Emptying facilities | [14 empty] | 11.4 | [5 empty] | 51 |  |  |  | 6 | 223.5294 |  |  | 0.15 |  | 6
|  |  | Surface Area | [6 empty] | m2 |  | 1319.4689 |  |  | Latent Heat |  |  |  |  | kJ/kg | * |  | false |  | (B.P) |  | F.P > 37.8 or B.P > 149 | [6 empty] | Underground Storage | [14 empty] | 22.7 | [5 empty] | 25 |  |  |  | 7 | 908 |  |  | 0.3 |  | 7
|  |  | Wetted Area for Emergency case | [6 empty] | m2 |  | 689.4414 |  |  | Relieving Temperature |  |  |  |  | °C | * | [5 empty] | F.P < 37.8 or B.P <149 | [6 empty] | Earth-covered storage above grade | [9 empty] | Underground storage | [18 empty] | 0
|  |  | Tank Location (Latitude) | [6 empty] | ° |  | 12.7 |  |  | Molecular mass of vapor | [5 empty] | * | [5 empty] | Unknown | [6 empty] | Impoundment away from tank | [9 empty] | Earth cover | [18 empty] | 0.3
|  |  | Design Pressure | [6 empty] | kPag |  | 101.32 |  |  | (* Required for emergency vent calculation, blank for Ref. Liquid = Hexane) | [7 empty] | false | [20 empty] | Impoundment | [18 empty] | 0.5
[10 empty] | CHK Design Pressure |  |  |  |  | DRAIN SYSTEM
[15 empty] | Drain line size |  |  |  |  | mm | [5 empty] | find cone roof area | [7 empty] | Flash Point
[15 empty] | Maximum height above the drain line |  |  |  |  | mm | [6 empty] | h | = | 2 |  |  |  |  | Boiling Point
|  |  | Tank Design / Configulation |  |  |  |  | Insulated tank - Partial Insulation | [18 empty] | r | = | 12 | [36 empty] | Outbreathing | [5 empty] | Normal Venting Requirement for thermal effect
[27 empty] | S | = | 12.1655 | [37 empty] | Normal |  |  |  |  | Tank capacity | Inbreathing | Outbreathing
[15 empty] | Total Tank Surface Area (shell+roof) |  |  |  |  | m2 | [6 empty] | A1 | = | 458.6295 | [37 empty] | Sequence |  | Capacity | Value |  |  |  | FP >= 37.8 or BP >=149 |  | other
[15 empty] | Insulated surface area |  |  |  |  | m2 | [13 empty] | Common Insulation Mat |  |  |  | Avg. Thermal Conductivity | [5 empty] | Thermal Outbreath - Yfactor | [22 empty] | 15 |  | 6000 | 538 | 1 | 10 | 1.69 | 1.01 |  | 1.69 | 1
|  |  | STREAM FLOWRATE | [34 empty] | W/m-K | [5 empty] | Latitude |  |  |  |  | Y-Factor | [17 empty] | 16 |  | 10000 | 726 | 2 | 20 | 3.38 | 2.02 |  | 3.38 | 2
[5 empty] | Incoming Streams | [10 empty] | Outgoing Streams | [17 empty] | Cellular Glass |  |  |  | 0.05 | [5 empty] | below 42° |  |  |  |  | 0.32 | [18 empty] | Pro rate |  | 628.0902 | 3 | 100 | 16.9 | 10.1 |  | 16.9 | 3
[5 empty] | Steam No. | [5 empty] | Flowrate (m3/h) |  |  |  |  | Steam No. |  |  |  | Flowrate (m3/h) | [13 empty] | Mineral Fiber |  |  |  | 0.04 | [5 empty] | Between 42 ° and 58° |  |  |  |  | 0.25 | [17 empty] | Other |  |  |  | 4 | 200 | 33.8 | 20.3 |  | 33.8 | 4
|  |  |  | 1. | [10 empty] | 1. | Rated flow of P-3120A/R |  |  |  | 149.7 | [13 empty] | Calcium Silicate |  |  |  | 0.06 | [5 empty] | Above 58° |  |  |  |  | 0.2 | [17 empty] | Sequence |  | Capacity | Value | 5 | 300 | 50.4 | 30.4 |  | 50.4 | 5
|  |  |  | 2. | [10 empty] | 2. | Rated flow of P-3120B/C |  |  |  | 219.2 | [13 empty] | Perlite |  |  |  | 0.07 | [28 empty] | 15 |  | 6000 | 896 | 6 | 500 | 84.4 | 50.7 |  | 84.5 | 6
|  |  |  | 3. | [10 empty] | 3. | [28 empty] | Thermal Inbreath - Cfactor | [22 empty] | 16 |  | 10000 | 1210 | 7 | 700 | 118 | 71 |  | 118 | 7
|  |  |  | 4. | [10 empty] | 4. | [28 empty] | Latitude |  |  |  |  | Vapor pressure | [18 empty] | Pro rate |  | 1046.4699 | 8 | 1000 | 169 | 101 |  | 169 | 8
|  |  |  | 5. | [10 empty] | 5. | [34 empty] | 1217 | [20 empty] | 9 | 1500 | 254 | 152 |  | 254 | 9
|  |  |  | 6. | [10 empty] | 6. | [34 empty] | 1521 | [20 empty] | 10 | 2000 | 338 | 203 |  | 338 | 10
|  |  |  | 7. | [10 empty] | 7. | [34 empty] | 1825 | [20 empty] | 11 | 3000 | 507 | 304 |  | 507 | 11
|  |  |  | 8. | [10 empty] | 8. | [34 empty] | 2130 | [15 empty] | Inbreathing |  |  |  |  | 12 | 3180 | 537 | 322 |  | 537 | 12
|  |  |  | 9. | [10 empty] | 9. | [34 empty] | 2434 | [16 empty] | Normal |  |  |  | 13 | 4000 | 647 | 388 |  | 647 | 13
|  |  |  | 10. | [10 empty] | 10. | [33 empty] | Heaxane |  |  |  |  | more than hexane or unknown | [12 empty] | Sequence |  | Capacity | Value | 14 | 5000 | 787 | 472 |  | 787 | 14
[9 empty] | TOTAL | [9 empty] | TOTAL | 368.9 | [28 empty] | <25 |  |  | >= 25 |  | <25 |  |  | >= 25 | [9 empty] | 15 |  | 6000 | 896 | 15 | 6000 | 896 | 538 |  | 896 | 15
[44 empty] | below 42° |  |  |  |  | 4 |  |  | 6.5 |  | 6.5 |  |  | 6.5 | [9 empty] | 16 |  | 10000 | 1210 | 16 | 10000 | 1210 | 726 |  | 1210 | 16
[35 empty] | Calc Ri | [8 empty] | Between 42 ° and 58° |  |  |  |  | 3 |  |  | 5 |  | 5 |  |  | 5 | [10 empty] | Pro rate |  | 1046.4699 | 17 | 12000 | 1345 | 807 |  | 1345 | 17
[36 empty] | (Fill Value) | [7 empty] | Above 58° |  |  |  |  | 2.5 |  |  | 4 |  | 4 |  |  | 4 | [13 empty] | 18 | 14000 | 1480 | 888 |  | 1480 | 18
|  | II. | CALCULATION | [32 empty] | 1 | [34 empty] | 19 | 16000 | 1615 | 969 |  | 1615 | 19
|  |  | NORMAL VENTING |  |  |  | Calculation Method : |  |  |  |  | API 2000 SEVENTH EDITION | [10 empty] | false | [20 empty] | Heat Input (Q) | [26 empty] | 20 | 18000 | 1750 | 1047 |  | 1750 | 20
[5 empty] | OUT-BREATHING | [11 empty] | INBREATHING | [5 empty] | false | [12 empty] | API 2000 FIFTH EDITION | [7 empty] | wetted surface area (ATWS) | [5 empty] | Design pressure kPag |  |  | Heat Input W (a*ATWS^n) | [17 empty] | 21 | 25000 | 2179 | 1307 |  | 2179 | 21
|  |  |  | 1. | Outbreathing Vol. Flowrate |  |  |  |  | Nm3/h | [5 empty] | 1. | Inbreathing Vol. Flowrate |  |  | Nm3/h |  | 368.9 | [13 empty] | API 2000 SIXTH EDITION | [16 empty] | a |  |  | n |  | a*ATWS^n | [12 empty] | 22 | 30000 | 2495 | 1497 |  | 2495 | 22
|  |  |  | 2. | Thermal out-breathing | [10 empty] | 2. | Thermal inbreating | [5 empty] | false | [12 empty] | API 2000 SEVENTH EDITION | [7 empty] | <18.6 | [5 empty] | <=103.4 |  |  | 63150 |  |  | 1 |  | 43538221.7189 | [12 empty] | 23 | 12000 | 1345 | 807 |  | 1345 | 23
[6 empty] | Y-Factor | [5 empty] | 0.32 | [5 empty] | C-Factor |  |  |  | 6.5 | false | [20 empty] | >=18.6 and <93 | [5 empty] | <=103.4 |  |  | 224200 |  |  | 0.566 |  | 9062021.7051 | [12 empty] | 24 | 14000 | 1480 | 888 |  | 1480 | 24
[6 empty] | Reduction factor | [5 empty] | #DIV/0! | [5 empty] | Reduction factor |  |  |  | #DIV/0! | [21 empty] | >=93 and <260 | [5 empty] | <=103.4 |  |  | 630400 |  |  | 0.338 |  | 5741538.7814 | [12 empty] | 25 | 16000 | 1615 | 969 |  | 1615 | 25
[6 empty] | Thermal out-breathing |  |  |  | Nm3/h |  | #DIV/0! | [5 empty] | Thermal inbreating |  | Nm3/h |  | #DIV/0! | #DIV/0! | #DIV/0! | [19 empty] | >=260 | [5 empty] | >7 and <103.4 |  |  | 43200 |  |  | 0.82 |  | 9184416.2623 | [12 empty] | 26 | 18000 | 1750 | 1047 |  | 1750 | 26
[5 empty] | Total normal out-breathing |  |  |  |  | Nm3/h | [6 empty] | Total normal inbreathing |  |  | Nm3/h |  | #DIV/0! | [21 empty] | >=260 | [5 empty] | <=7 |  |  | 4129700 |  |  | 0 |  | 4129700 | [12 empty] | 27 | 25000 | 2179 | 1307 |  | 2179 | 27
[23 empty] | false | [47 empty] | 28 | 30000 | 2495 | 1497 |  | 2495 | 28
|  |  | EMERGENCY VENTING | [40 empty] | Emergency Venting for fire exposure
EMERGENCY VENTING
|  |  | Heat input from Fire Exposure, Q | [10 empty] | 5741538.7814 | [5 empty] | W | [23 empty] | Wetted area (m2) (<=103.4) | [5 empty] | Venting Required (Nm3/h)
|  |  | Environmental factor, F | [10 empty] | 1 | [29 empty] | 2 | [5 empty] | 608
|  |  | Emergency Venting Required for Fire Exposure | [10 empty] | 28451.9358 | [5 empty] | Nm3/h of Air | [23 empty] | 3 | [5 empty] | 913
[44 empty] | 9 | [5 empty] | 2738
|  |  | DRAIN SYSTEM | [40 empty] | 11 | [5 empty] | 3347
|  |  | Inbreating requirement due to draining | [9 empty] | Nm3/h | [30 empty] | 13 | [5 empty] | 3955
[44 empty] | 15 | [5 empty] | 4563
[44 empty] | 17 | [5 empty] | 5172
|  | NOTE S: | [41 empty] | 19 | [5 empty] | 5780
[44 empty] | 22 | [5 empty] | 6217
[44 empty] | 25 | [5 empty] | 6684
[44 empty] | 30 | [5 empty] | 7411
[44 empty] | 35 | [5 empty] | 8086
[44 empty] | 40 | [5 empty] | 8721
[44 empty] | 45 | [5 empty] | 9322
[44 empty] | 50 | [5 empty] | 9895
[44 empty] | 60 | [5 empty] | 10971
[44 empty] | 70 | [5 empty] | 11971
[44 empty] | 80 | [5 empty] | 12911
[44 empty] | 90 | [5 empty] | 13801
[44 empty] | 110 | [5 empty] | 15461
[44 empty] | 130 | [5 empty] | 15751
[44 empty] | 150 | [5 empty] | 16532
[44 empty] | 175 | [5 empty] | 17416
[44 empty] | 200 | [5 empty] | 18220
[44 empty] | 230 | [5 empty] | 19102
[44 empty] | 260 | [5 empty] | 19910
[44 empty] | >260 (Design Pressure <=7) | [5 empty] | 19910
[44 empty] | >260 (Design Pressure >=7) | [5 empty] | 44263.7839
[42 empty] | Venting capacity (Nm3/h) incase of hexane properties | [7 empty] | 44263.7839
[44 empty] | Tank configuration | [5 empty] | Insulation conductance |  |  | Insulation thickness |  |  |  | F-factor
[50 empty] | W/m2K |  |  | cm
[44 empty] | Bare metal tank | [8 empty] | 0 |  |  |  | 1
[44 empty] | Insulated tank | [5 empty] | 22.7 |  |  | 2.5 |  |  |  | 0.3
[50 empty] | 11.4 |  |  | 5.1 |  |  |  | 0.15
[50 empty] | 5.7 |  |  | 10.2 |  |  |  | 0.075
[50 empty] | 3.8 |  |  | 15.2 |  |  |  | 0.05
[50 empty] | 2.8 |  |  | 20.3 |  |  |  | 0.0375
[50 empty] | 2.3 |  |  | 25.4 |  |  |  | 0.03
[50 empty] | 1.9 |  |  | 30.5 |  |  |  | 0.025
Liquid Properties
[39 empty] | 1A | NORMAL INBREATHING | [17 empty] | 2A | Normal outbreathing | [14 empty] | 3A | Emergency Vent
Hexane Vapor Pressure
[31 empty] | = | 30.6491 | kPa @ |  |  | 35 | C |  |  | 5th | [18 empty] | 5th
[41 empty] | Normal Inbreathing = 0.94*flow out | [18 empty] | Normal outbreathing |  |  |  | = | Check F.P or B.P | Nm3/h
[44 empty] | = | 346.766 |  | Nm3/h | [12 empty] | (See table 1B)
[40 empty] | 6th | [18 empty] | 6th
[41 empty] | Normal Inbreathing = Liquid Discharge | [18 empty] | Normal outbreathing |  |  |  | = |  | Nm3/h
[44 empty] | = | 368.9 |  | Nm3/h | [32 empty] | ???????
7th
[41 empty] | Normal Inbreathing = Liquid Discharge | [17 empty] | 7th
[44 empty] | = | 368.9 |  | Nm3/h | [12 empty] | Normal outbreathing
[39 empty] | 1B | Thermal Inbreathing | [19 empty] | Liquid ----> |  | Volatile Liquids
[40 empty] | 5th | [19 empty] | Normal outbreathing |  |  |  | = | #VALUE! | Nm3/h | [7 empty] | A (Wetted Surface Area) |  |  |  | 689.4414 | m2
[41 empty] | From table | [32 empty] | Q (heat input from fire exposure) |  |  |  | 5741538.7814 | W
[41 empty] | Vit |  |  | = | 1046.4699 |  | Nm3/h | [26 empty] | F (environmental factor -obtain from API Standard 2000) |  |  |  | 1
[58 empty] | 2B | Thermal outbreathing | [14 empty] | L (latent heat of vap of stored liquid at relieving P & T) |  |  |  | 334.9 | kJ/kg
[40 empty] | 6th | [18 empty] | 5th | [14 empty] | T (temp of relieving vapour - normally Tbp at relieving P) |  |  |  | 15.6 | oC
[60 empty] | From Table | [13 empty] | M.W |  |  |  | 86.17 | g/mol
[60 empty] | Vot |  |  |  | = | Chk F.P/B.P | Nm3/h | [7 empty] | P (Design Tank Pressure) |  |  |  | 101.32 | kPag
[74 empty] | Emergency Venting Required For Fire Exposure |  |  |  | 28451.9358 | Nm3/h of air
6th
[61 empty] | Y |  |  | = | 0.32
[61 empty] | Ri |  |  | = | #DIV/0!
[61 empty] | Vot |  |  | = | #DIV/0! | Nm3/h
7th
[43 empty] | C | = | 6.5 | [14 empty] | same 6th
[43 empty] | Rin | = | #DIV/0! |  |  | Rinp |  | = | #DIV/0!
[43 empty] | Vit | = | #DIV/0! | Nm3/h
7th
- Same 6th
Note on AD10: Optional input, for reference only.
Note on AF10: if both available (VP vs FP), use flash point-this criteria is used in API2000 5th only.
Note on AF12: Normally Boiling point at relieving Pressure
Note on O13: As find in Google map (Latitude,Longitude) Typical for Maptaput, Thailand is 12.7° (Thailand : 5.6°-20.4°)
Note on O14: Design pressure must be lower than 103.4 kPag.
Note on AF17: Maximum liquid level
Note on AF19: Commonly assumed as 4 W/m2-K for typical tanks
Note on U52: The environmental factor, F, is taken as 1.0 for bare-metal tanks. For insulated tanks, F varies between 0.025 and 0.30, depending upon the insulation conductance. The details are furnished in API 2000, Table 9.